## Base
Instrument | Device Module Object | Device Module Class | Digital In 1 | DM Digital Out 1 | Analog In 1 | Analog Out 1 | Fieldbus | sub-assembly/position | Description | Manufacturer | Reference | Signal | Power | Control value(s) / Unit(s) / Range | Measured value(s) / Unit(s) / Range(s) | Tag Number | I/O module | I/O module description | Slot
BL-1 | dmBL_1 | DM_BL_DO |  | 1 |  |  |  |  | Piston pump, blower 8009-35/05/DC | Thomas | 80091020 |  | 12VDC & 5A | Status / On-Off / - Motor speed / rpm / 0-2800 | Pressure (P-2) / Bars / 0-2 | PLC_3 | EL2008 | 8x DO 0-24VDC, 0.5A | 5
BL-2 | dmBL_2 | DM_BL_DO |  | 1 |  |  |  |  | Piston pump, blower 8009-35/05/DC | Thomas | 80091020 |  | 12VDC & 5A | Status / On-Off / - Motor speed / rpm / 0-2800 | Pressure (MFM-5) / Bars / 0-2 | PLC_3 | EL2008 | 8x DO 0-24VDC, 0.5A | 5
C-1 | dmC_DO | DM_C_DO |  | 1 |  |  |  |  | Compressor 405 Series | Thomas | 405ADC38/12 |  | 12VDC & 10.5A | Status / On-Off / - Motor speed / rpm / 0-1500 |  | PLC_3 | EL2008 | 8x DO 0-24VDC, 0.5A | 5
CO2-1 | dmCO2_1 | DM_Hamilton_485 |  |  |  |  | Modbus | Feed | CO2 sensor - 0-100% | Hamilton | CO2NTROL RS485 120 + 1M DATA CABLE VP8 / OPEN EN | Modbus | 10…27VDC | CO₂ concentration unit / %-vol Temperature / °C /0-60°C | CO₂ concentration / %-vol / 0-100 | PLC_8 | EL6022 | 2-port RS-485 junction | 10
CO2-2 | dmCO2_2 | DM_Hamilton_485 |  |  |  |  | Modbus | Feed+Retentate 2 | CO2 sensor - 0-100% | Hamilton | CO2NTROL RS485 120 + 1M DATA CABLE VP8 / OPEN EN | Modbus | 10…27VDC | CO₂ concentration unit / %-vol Temperature / °C /0-60°C | CO₂ concentration / %-vol / 0-100 | PLC_8 | EL6022 | 2-port RS-485 junction | 10
CO2-3 | dmCO2_3 | DM_SmartGas_485 |  |  |  |  | Modbus | Retentate 1 | CO2 sensor 0-20% | Smartgas | F3-212207-05000 | Modbus | 3.3…6VDC |  | CO₂ concentration / %-vol / 0-20 | PLC_8 | EL6022 | 2-port RS-485 junction | 10
CO2-4 | dmCO2_4 | DM_Hamilton_485 |  |  |  |  | Modbus | Permeate 1 | CO2 sensor - 100% | Hamilton | CO2NTROL RS485 120 + 1M DATA CABLE VP8 / OPEN EN | Modbus | 10…27VDC | CO₂ concentration unit / %-vol Temperature / °C /0-60°C | CO₂ concentration / %-vol / 0-100 | PLC_8 | EL6022 | 2-port RS-485 junction | 10
CO2-5 | dmCO2_5 | DM_SmartGas_485 |  |  |  |  | Modbus | Permeate 2 | CO2 sensor - 100% | Smartgas | F3-212108-05000 | Modbus | 3.3…6VDC |  | CO₂ concentration / %-vol / 0100%
Emergency stop button |  | DM_E_Stop_In | 1 |  |  |  |  | Electrical cabinet | [6 empty] | Status / On-Off / - | PLC_1 | EL1008 | 4x DI 0-24VDC | 3
H-1 |  | ? | [6 empty] | Humidifier | Bronkhorst | W-102A-122-P |  |  | ? | ?
HE-1 | dmHE_1 | DM_Heater |  | 1 |  |  |  |  | Heating element 1 - feed (+retentate 1) before membrane module 1 | Acim Jouanin | RCF 630 |  | 230VAC | Temperature / °C /0-100°C |  | PLC_14 | EL2602 | 2x Relay output 230 V AC, 30 V DC, 5 A | 17
HE-2 | dmHE_2 | DM_Heater |  | 1 |  |  |  |  | Heating element 2 - membrane module 1 | Acim Jouanin | H10X100X500 |  | 230VAC | Temperature / °C /0-180°C |  | PLC_14 | EL2602 | 2x Relay output 230 V AC, 30 V DC, 5 A | 17
HE-3 | dmHE_3 | DM_Heater |  | 1 |  |  |  |  | Heating element 3 - retentate 1 | Acim Jouanin | RCF 630 |  | 230VAC | Temperature / °C /0-100°C |  | PLC_15 | EL2602 | 2x Relay output 230 V AC, 30 V DC, 5 A | 18
HE-4 | dmHE_4 | DM_Heater |  | 1 |  |  |  |  | Heating element - membrane module 2 | Acim Jouanin | H10X100X500 |  | 230VAC | Temperature / °C /0-180°C |  | PLC_15 | EL2602 | 2x Relay output 230 V AC, 30 V DC, 5 A | 18
HE-5 | dmHE_5 | DM_Heater |  | 1 |  |  |  |  | Heating element - humidifier stream, feed (+retentate 1) after humidifier | Acim Jouanin | RCF 630 |  | 230VAC | Temperature / °C /0-100°C
MFC-1 | dmMFC_1 | DM_MFC_Voegtlin_EC |  |  |  |  | EtherCAT | Feed | Massflow controller - CO2 2l/min | Vögtlin | K5WP6RK4-000000 | EtherCAT | 24VDC | Flow rate / slpm / 0-5 | Pressure /bars / 0-6 Temperature /°C/0-40°C | PLC_6 | EK1122 | 2-port EtherCAT junction | 8
MFC-2 | dmMFC_2 | DM_MFC_Voegtlin_EC |  |  |  |  | EtherCAT | Feed | Massflow controller - N2 5l/min | Vögtlin | P4XX7VM4-000000 | EtherCAT | 24VDC | Flow rate / slpm / 0-5 | Pressure /bars / 0-6 Temperature /°C/0-40°C | PLC_7 | EK1123 | 2-port EtherCAT junction | 8
MFC-3 | dmMFC_3 | DM_MFC_Voegtlin_EC |  |  |  |  | EtherCAT | Feed | Massflow controller - O2 1l/min | Vögtlin | 93YY8W83-000000 | EtherCAT | 24VDC | Flow rate / slpm / 0-5 | Pressure /bars / 0-6 Temperature /°C/0-40°C | PLC_8 | EK1124 | 2-port EtherCAT junction | 8
MFC-4 | dmMFC_4 | DM_MFC_Voegtlin_EC |  |  |  |  | EtherCAT | Feed | Massflow controller - Flue gas | Vögtlin | 321-4122 | EtherCAT | 24VDC | Flow rate / slpm / 0-5 | Pressure /bars / 0-6 Temperature /°C/0-40°C | PLC_9 | EK1125 | 2-port EtherCAT junction | 8
MFC-5 | dmMFC_5 | DM_MFC_Voegtlin_EC |  |  |  |  | EtherCAT |  | Mass flow controller - Water for humidifier
MFM-1 | dmMFM_1 | DM_MFM_Voegtlin_EC |  |  |  |  | EtherCAT | Feed | Mass flow meter with pressure regulator - feed | Vögtlin | GSP-C3KA-BB26 |  |  | Pressure /bars / 0-6 | Flow rate /splm / 0-5 Temperature /°C/0-40
MFM-2 | dmMFM_2 | DM_MFM_Voegtlin_EC |  |  |  |  | EtherCAT | Feed+Retentate 2 | Mass flow meter - feed (+ retentate 2) | Vögtlin | GSM-C9KA-BN00 |  |  |  | Flow rate /splm / 0-5 Temperature /°C/0-40 Pressure / bars /0-6
MFM-3 | dmMFM_3 | DM_MFM_Voegtlin_EC |  |  |  |  | EtherCAT | Retentate 1 | Mass flow meter with back pressure regulator - retentate 1 | Vögtlin | GSP-C9KA-BB26 |  |  | Pressure /bars / 0-6 | Flow rate /splm / 0-5 Temperature /°C/0-40
MFM-4 | dmMFM_4 | DM_MFM_Voegtlin_EC |  |  |  |  | EtherCAT | Permeate 1 | Mass flow meter - permeate 1 | Vögtlin | GSM-C9KA-BN00 |  |  |  | Flow rate /splm / 0-5 Temperature /°C/0-40 Pressure / bars /0-6
MFM-5 | dmMFM_5 | DM_MFM_Voegtlin_EC |  |  |  |  | EtherCAT | Permeate 2 | Mass flow meter - permeate 2 | Vögtlin | GSM-C9KA-BN00 |  |  |  | Flow rate /splm / 0-5 Temperature /°C/0-40 Pressure / bars /0-6
MFM-6 | dmMFM_6 | DM_MFM_Voegtlin_EC |  |  |  |  | EtherCAT | retentate 2 | Mass flow meter with back pressure regulator - retentate 2 | Vögtlin | GSP-C9KA-BB26 |  |  | Pressure /bars / 0-6 | Flow rate /splm / 0-5 Temperature /°C/0-40
P-1 | dmP_1 | DM_P_Wika_AI_1 |  |  | 1 |  |  | Vacuum pump 1 | Pressure sensor with transmitter - permeate 1 before vacuum pump 1 | Wika | A-10-6-BV325-NBZZ-AA-AGZ-ZW | 4…20mA | 8…30VDC |  | Pressure /bars / -1…1.5 | PLC_4 | EL3054 | 4x AI 4-20mA single ended | 6
P-2 | dmP_2 | DM_P_Wika_AI_1 |  |  | 1 |  |  | Permeate 1 | Pressure sensor with transmitter - permeate 1 after blower before membrane 2 | Wika | 46879286 | 4…20mA | 8…30VDC |  | Pressure /bars / 0…6 | PLC_4 | EL3054 | 4x AI 4-20mA single ended | 6
P-3 | dmP_3 | DM_P_Wika_AI_1 |  |  | 1 |  |  | Vacuum pump 2 | Pressure sensor with transmitter - permeate 2 before vacuum pump 2 | Wika | A-10-6-BV325-NBZZ-AA-AGZ-ZW | 4…20mA | 8…30VDC |  | Pressure /bars / -1…1.5 | PLC_4 | EL3054 | 4x AI 4-20mA single ended | 6
P-4 | dmP_4 | DM_P_Wika_AI_1 |  |  | 1 |  |  | retentate 2 | Pressure sensor with transmitter - retentate 2 after compressor | Wika | 46879286 | 4…20mA | 8…30VDC |  | Pressure /bars / 0…6 | PLC_4 | EL3054 | 4x AI 4-20mA single ended | 6
RH-1 | dmRH_1 | DM_Vaisala_485 |  |  |  |  | Modbus |  | Relative humidity sensor | Vaisala | HMP7 | RS485 modbus | 18…30VDC |  | Relative humidity / % / 0-100 Temperature /°C /0-100 | PLC_9 | EL6022 | 2-port RS-485 junction | 11
Signal tower | dmSignalTower | DM_SignalTower_3 |  | 3 |  |  |  | Frame | Signal tower, 3 colors, status indicator | Werma | 698.110.75 |  | 24VDC | Flash_Green Flash_Yellow Flash_Red |  | PLC_3 | EL2008 | 8x DO 0-24VDC, 0.5A | 5
SV-1 | dmSV_1 | DM_Svalve | [5 empty] | Feed | Safety solenoïd valve - CO2 | Bürkert | Typ 6013 A - 126082 | - | 24VDC | Status / On-Off / - | Status / On-Off / - | PLC_2 | EL2008 | 8x DO 0-24VDC, 0.5A | 4
SV-2 | dmSV_2 | DM_Svalve | [5 empty] | Feed | Safety solenoïd valve - N2 | Bürkert | Typ 6013 A - 126082 | - | 24VDC | Status / On-Off / - | Status / On-Off / - | PLC_2 | EL2008 | 8x DO 0-24VDC, 0.5A | 4
SV-3 | dmSV_3 | DM_Svalve | [5 empty] | Feed | Safety solenoïd valve - O2 | Bürkert | Typ 6013 A - 126082 | - | 24VDC | Status / On-Off / - | Status / On-Off / - | PLC_2 | EL2008 | 8x DO 0-24VDC, 0.5A | 4
SV-4 | dmSV_4 | DM_Svalve | [5 empty] | Feed | Safety solenoïd valve - Flue gas | Bürkert | Typ 6013 A - 126082 | - | 24VDC | Status / On-Off / - | Status / On-Off / - | PLC_2 | EL2008 | 8x DO 0-24VDC, 0.5A | 4
SV-5 | dmSV_5 | [6 empty] | Humidifier | Safety solenoïd valve - Water inlet for humidifier | Bürkert | Typ 6013 A - 126082 | - | 24VDC | Status / On-Off / - | Status / On-Off / -
T-1 | dm_T1 | DM_TC_AI |  |  | 1 |  |  |  | Temperature transmitter - heating element feed before membrane module | EMKO | TCS-M06-L060-K02.K |  |  |  | Temperature /°C /0-100 | PLC-11 | EL3314 | 4x AI thermocouple | 14
T-2 | dm_T2 | DM_TC_AI |  |  | 1 |  |  |  | Temperature transmitter- feed before membrane module 1 | EMKO | TCS-M06-L060-K02.K |  |  |  | Temperature /°C /0-100 | PLC-11 | EL3314 | 4x AI thermocouple | 14
T-3 | dm_T3 | DM_TC_AI |  |  | 1 |  |  |  | Temperature transmitter - heating element membrane module 1 | EMKO | TCS-M06-L060-K02.K |  |  |  | Temperature /°C /0-180 | PLC-11 | EL3314 | 4x AI thermocouple | 14
T-4 | dm_T4 | DM_TC_AI |  |  | 1 |  |  | Vacuum pump 1 | Temperature transmitter - permeate 1 | RS-PRO | 824-0587 |  |  |  | Temperature /°C /0-100 | PLC-11 | EL3314 | 4x AI thermocouple | 14
T-5 | dm_T5 | DM_TC_AI |  |  | 1 |  |  |  | Temperature transmitter - heating element retentate 1 | EMKO | TCS-M06-L060-K02.K |  |  |  | Temperature /°C /0-100 | PLC_12 | EL3314 | 4x AI thermocouple | 15
T-6 | dm_T6 | DM_TC_AI |  |  | 1 |  |  | Permeate 1 | Temperature transmitter - feed before membrane module 2 | EMKO | TCS-M06-L060-K02.K |  |  |  | Temperature /°C /0-100 | PLC_12 | EL3314 | 4x AI thermocouple | 15
T-7 | dm_T7 | DM_TC_AI |  |  | 1 |  |  |  | Temperature transmitter - heating element membrane module 2 | EMKO | TCS-M06-L060-K02.K |  |  |  | Temperature /°C /0-180 | PLC_12 | EL3314 | 4x AI thermocouple | 15
T-8 | dm_T8 | DM_TC_AI |  |  | 1 |  |  | retentate 2 | Temperature transmitter - retentate 2 after compressor | EMKO | TCS-M06-L060-K02.K |  |  |  | Temperature /°C /0-100 | PLC_12 | EL3314 | 4x AI thermocouple | 15
T-9 | dm_T9 | DM_TC_AI |  |  | 1 |  |  |  | Temperature transmitter - heating element humidifier | EMKO | TCS-M06-L060-K02.K |  |  |  | Temperature /°C /0-100 | PLC_13 | EL3314 | 4x AI thermocouple | 16
T-10 | dm_T10 | DM_TC_AI |  |  | 1 |  |  | Humidifier | Temperature transmitter - feed after humidifier | EMKO | TCS-M06-L060-K02.K |  |  |  | Temperature /°C /0-100 | PLC_13 | EL3314 | 4x AI thermocouple | 16
T-11 | dm_T11 | DM_TC_AI |  |  | 1 |  |  |  | Temperature transmitter - heating element feed after humidifier | EMKO | TCS-M06-L060-K02.K |  |  |  | Temperature /°C /0-100 | PLC_13 | EL3314 | 4x AI thermocouple | 16
TI-1 | [8 empty] | Digital indicator thermocouple | EMKO | ESM-3710-N.8.10.0.2/00.00/1.0.0.0 | RS485 modbus | 24VDC |  |  | PLC_9 | EL6022 | 2-port RS-485 junction | 11
TI-2 | [8 empty] | Digital indicator thermocouple | EMKO | ESM-3710-N.8.10.0.2/00.00/1.0.0.0 | RS485 modbus | 24VDC |  |  | PLC_9 | EL6022 | 2-port RS-485 junction | 11
TI-3 | [8 empty] | Digital indicator thermocouple | EMKO | ESM-3710-N.8.10.0.2/00.00/1.0.0.0 | RS485 modbus | 24VDC |  |  | PLC_9 | EL6022 | 2-port RS-485 junction | 11
TI-4 | [7 empty] | Permeate 1 | Digital indicator thermocouple | EMKO | ESM-3710-N.8.10.0.2/00.00/1.0.0.0 | RS485 modbus | 24VDC |  |  | PLC_9 | EL6022 | 2-port RS-485 junction | 11
TI-5 | [8 empty] | Digital indicator thermocouple | EMKO | ESM-3710-N.8.10.0.2/00.00/1.0.0.0 | RS485 modbus | 24VDC |  |  | PLC_9 | EL6022 | 2-port RS-485 junction | 11
TI-6 | [7 empty] | retentate 2 | Digital indicator thermocouple | EMKO | ESM-3710-N.8.10.0.2/00.00/1.0.0.0 |  |  |  |  | PLC_9 | EL6022 | 2-port RS-485 junction | 11
VP-1 | dmVP_1 | DM_VP_Pfeifer |  | 1 |  |  |  | Vacuum pump 1 | Vacuum pump, membrane module 1 2000026533 HiScroll Expert Bundle including: HiScroll 18, Omnicontrol 001 with 1 Gauge I/O, exhaust silencer ES 25 L incl. clamps, interface cable and M12 adapter Best for use in quiet environments such as in the laboratory ‒ Pumping speed: 18.1 m³ / h ‒ Ultimate pressure without gas ballast: 7e-3 mbar No venting when stoped due to intgrated check valve ‒ Very low noise level: < 47 dB(A) ‒ Light weight: 23 kg ‒ Integrated Pressure sensor RPT 010 ‒ Interface: RS-485, compatible to Omnicontrol (turbo pump) ‒ Rotation speed variable: 40 - 100% ‒ Active intelligent air-cooling Additional data according brochure ‒ Old Material Number: PD 100 185 -T | PfeifferVacuum | PD-S30-010 | RS-485 | 100…240VAC | Status / On-Off / - |  | PLC_3 | EL2008 | 8x DO 0-24VDC, 0.5A | 5
[7 empty] | ASCII | [6 empty] | Power / % /0-100 | Status / On-Off / - | PLC_7 | EL6022 | 2-port RS-485 junction | 9
VP-2 | dmVP_2 | DM_VP_Pfeifer |  | 1 |  |  |  | Vacuum pump 2 | Vacuum pump, membrane module 2 2000026533 HiScroll Expert Bundle including: HiScroll 18, Omnicontrol 001 with 1 Gauge I/O, exhaust silencer ES 25 L incl. clamps, interface cable and M12 adapter Best for use in quiet environments such as in the laboratory ‒ Pumping speed: 18.1 m³ / h ‒ Ultimate pressure without gas ballast: 7e-3 mbar No venting when stoped due to intgrated check valve ‒ Very low noise level: < 47 dB(A) ‒ Light weight: 23 kg ‒ Integrated Pressure sensor RPT 010 ‒ Interface: RS-485, compatible to Omnicontrol (turbo pump) ‒ Rotation speed variable: 40 - 100% ‒ Active intelligent air-cooling Additional data according brochure ‒ Old Material Number: PD 100 185 -T | PfeifferVacuum | PD-S30-010 | RS-485 | 100…240VAC | Status / On-Off / - |  | PLC_3 | EL2008 | 8x DO 0-24VDC, 0.5A | 5
[7 empty] | ASCII | [6 empty] | Power / % /0-100 | Status / On-Off / - | PLC_7 | EL6022 | 2-port RS-485 junction | 9
Note on O4: [Commentaire à thread] Votre version d’Excel vous permet de lire ce commentaire à thread. Toutefois, les modifications qui y sont apportées seront supprimées si le fichier est ouvert dans une version plus récente d’Excel. En savoir plus : https://go.microsoft.com/fwlink/?linkid=870924 Commentaire : Il faut ajouter un controleur moteur pour chacun de ces éléments, je ne sais pas si c’est disponible chez Beckhoff
Note on O6: [Commentaire à thread] Votre version d’Excel vous permet de lire ce commentaire à thread. Toutefois, les modifications qui y sont apportées seront supprimées si le fichier est ouvert dans une version plus récente d’Excel. En savoir plus : https://go.microsoft.com/fwlink/?linkid=870924 Commentaire : Les capteurs de CO2 smart gas et hamilton doivent être calibrés. La mesure dépend de la température et de la pression.

## Abstract
Instrument | Device Module Object | Device Module Class | Fieldbus | Description | Measured value(s) / Unit(s) / Range(s) | I/O module | Slot
BL-1 | dmBL_1 | DM_BL_DO |  | Piston pump, blower 8009-35/05/DC | Pressure (P-2) / Bars / 0-2 | EL2008 | 5
BL-2 | dmBL_2 | DM_BL_DO |  | Piston pump, blower 8009-35/05/DC | Pressure (MFM-5) / Bars / 0-2 | EL2008 | 5
C-1 | dmC_DO | DM_C_DO |  | Compressor 405 Series |  | EL2008 | 5
CO2-1 | dmCO2_1 | DM_Hamilton_485 | Modbus | CO2 sensor - 0-100% | CO₂ concentration / %-vol / 0-100 | EL6022 | 10
CO2-2 | dmCO2_2 | DM_Hamilton_485 | Modbus | CO2 sensor - 0-100% | CO₂ concentration / %-vol / 0-100 | EL6022 | 10
CO2-3 | dmCO2_3 | DM_SmartGas_485 | Modbus | CO2 sensor 0-20% | CO₂ concentration / %-vol / 0-20 | EL6022 | 10
CO2-4 | dmCO2_4 | DM_Hamilton_485 | Modbus | CO2 sensor - 100% | CO₂ concentration / %-vol / 0-100 | EL6022 | 10
CO2-5 | dmCO2_5 | DM_SmartGas_485 | Modbus | CO2 sensor - 100% | CO₂ concentration / %-vol / 0100%
Emergency stop button |  | DM_E_Stop_In |  |  | Status / On-Off / - | EL1008 | 3
H-1 |  | ? |  | Humidifier | ?
HE-1 | dmHE_1 | DM_Heater |  | Heating element 1 - feed (+retentate 1) before membrane module 1 |  | EL2602 | 17
HE-2 | dmHE_2 | DM_Heater |  | Heating element 2 - membrane module 1 |  | EL2602 | 17
HE-3 | dmHE_3 | DM_Heater |  | Heating element 3 - retentate 1 |  | EL2602 | 18
HE-4 | dmHE_4 | DM_Heater |  | Heating element - membrane module 2 |  | EL2602 | 18
HE-5 | dmHE_5 | DM_Heater |  | Heating element - humidifier stream, feed (+retentate 1) after humidifier
MFC-1 | dmMFC_1 | DM_MFC_Voegtlin_EC | EtherCAT | Massflow controller - CO2 2l/min | Pressure /bars / 0-6 Temperature /°C/0-40°C | EK1122 | 8
MFC-2 | dmMFC_2 | DM_MFC_Voegtlin_EC | EtherCAT | Massflow controller - N2 5l/min | Pressure /bars / 0-6 Temperature /°C/0-40°C | EK1123 | 8
MFC-3 | dmMFC_3 | DM_MFC_Voegtlin_EC | EtherCAT | Massflow controller - O2 1l/min | Pressure /bars / 0-6 Temperature /°C/0-40°C | EK1124 | 8
MFC-4 | dmMFC_4 | DM_MFC_Voegtlin_EC | EtherCAT | Massflow controller - Flue gas | Pressure /bars / 0-6 Temperature /°C/0-40°C | EK1125 | 8
MFC-5 | dmMFC_5 | DM_MFC_Voegtlin_EC | EtherCAT | Mass flow controller - Water for humidifier
MFM-1 | dmMFM_1 | DM_MFM_Voegtlin_EC | EtherCAT | Mass flow meter with pressure regulator - feed | Flow rate /splm / 0-5 Temperature /°C/0-40
MFM-2 | dmMFM_2 | DM_MFM_Voegtlin_EC | EtherCAT | Mass flow meter - feed (+ retentate 2) | Flow rate /splm / 0-5 Temperature /°C/0-40 Pressure / bars /0-6
MFM-3 | dmMFM_3 | DM_MFM_Voegtlin_EC | EtherCAT | Mass flow meter with back pressure regulator - retentate 1 | Flow rate /splm / 0-5 Temperature /°C/0-40
MFM-4 | dmMFM_4 | DM_MFM_Voegtlin_EC | EtherCAT | Mass flow meter - permeate 1 | Flow rate /splm / 0-5 Temperature /°C/0-40 Pressure / bars /0-6
MFM-5 | dmMFM_5 | DM_MFM_Voegtlin_EC | EtherCAT | Mass flow meter - permeate 2 | Flow rate /splm / 0-5 Temperature /°C/0-40 Pressure / bars /0-6
MFM-6 | dmMFM_6 | DM_MFM_Voegtlin_EC | EtherCAT | Mass flow meter with back pressure regulator - retentate 2 | Flow rate /splm / 0-5 Temperature /°C/0-40
P-1 | dmP_1 | DM_P_Wika_AI_1 |  | Pressure sensor with transmitter - permeate 1 before vacuum pump 1 | Pressure /bars / -1…1.5 | EL3054 | 6
P-2 | dmP_2 | DM_P_Wika_AI_1 |  | Pressure sensor with transmitter - permeate 1 after blower before membrane 2 | Pressure /bars / 0…6 | EL3054 | 6
P-3 | dmP_3 | DM_P_Wika_AI_1 |  | Pressure sensor with transmitter - permeate 2 before vacuum pump 2 | Pressure /bars / -1…1.5 | EL3054 | 6
P-4 | dmP_4 | DM_P_Wika_AI_1 |  | Pressure sensor with transmitter - retentate 2 after compressor | Pressure /bars / 0…6 | EL3054 | 6
RH-1 | dmRH_1 | DM_Vaisala_485 | Modbus | Relative humidity sensor | Relative humidity / % / 0-100 Temperature /°C /0-100 | EL6022 | 11
Signal tower | dmSignalTower | DM_SignalTower_3 |  | Signal tower, 3 colors, status indicator |  | EL2008 | 5
SV-1 | dmSV_1 | DM_Svalve |  | Safety solenoïd valve - CO2 | Status / On-Off / - | EL2008 | 4
SV-2 | dmSV_2 | DM_Svalve |  | Safety solenoïd valve - N2 | Status / On-Off / - | EL2008 | 4
SV-3 | dmSV_3 | DM_Svalve |  | Safety solenoïd valve - O2 | Status / On-Off / - | EL2008 | 4
SV-4 | dmSV_4 | DM_Svalve |  | Safety solenoïd valve - Flue gas | Status / On-Off / - | EL2008 | 4
SV-5 | dmSV_5 |  |  | Safety solenoïd valve - Water inlet for humidifier | Status / On-Off / -
T-1 | dm_T1 | DM_TC_AI |  | Temperature transmitter - heating element feed before membrane module | Temperature /°C /0-100 | EL3314 | 14
T-2 | dm_T2 | DM_TC_AI |  | Temperature transmitter- feed before membrane module 1 | Temperature /°C /0-100 | EL3314 | 14
T-3 | dm_T3 | DM_TC_AI |  | Temperature transmitter - heating element membrane module 1 | Temperature /°C /0-180 | EL3314 | 14
T-4 | dm_T4 | DM_TC_AI |  | Temperature transmitter - permeate 1 | Temperature /°C /0-100 | EL3314 | 14
T-5 | dm_T5 | DM_TC_AI |  | Temperature transmitter - heating element retentate 1 | Temperature /°C /0-100 | EL3314 | 15
T-6 | dm_T6 | DM_TC_AI |  | Temperature transmitter - feed before membrane module 2 | Temperature /°C /0-100 | EL3314 | 15
T-7 | dm_T7 | DM_TC_AI |  | Temperature transmitter - heating element membrane module 2 | Temperature /°C /0-180 | EL3314 | 15
T-8 | dm_T8 | DM_TC_AI |  | Temperature transmitter - retentate 2 after compressor | Temperature /°C /0-100 | EL3314 | 15
T-9 | dm_T9 | DM_TC_AI |  | Temperature transmitter - heating element humidifier | Temperature /°C /0-100 | EL3314 | 16
T-10 | dm_T10 | DM_TC_AI |  | Temperature transmitter - feed after humidifier | Temperature /°C /0-100 | EL3314 | 16
T-11 | dm_T11 | DM_TC_AI |  | Temperature transmitter - heating element feed after humidifier | Temperature /°C /0-100 | EL3314 | 16
TI-1 |  |  |  | Digital indicator thermocouple |  | EL6022 | 11
TI-2 |  |  |  | Digital indicator thermocouple |  | EL6022 | 11
TI-3 |  |  |  | Digital indicator thermocouple |  | EL6022 | 11
TI-4 |  |  |  | Digital indicator thermocouple |  | EL6022 | 11
TI-5 |  |  |  | Digital indicator thermocouple |  | EL6022 | 11
TI-6 |  |  |  | Digital indicator thermocouple |  | EL6022 | 11
VP-1 | dmVP_1 | DM_VP_Pfeifer |  | Vacuum pump, membrane module 1 2000026533 HiScroll Expert Bundle including: HiScroll 18, Omnicontrol 001 with 1 Gauge I/O, exhaust silencer ES 25 L incl. clamps, interface cable and M12 adapter Best for use in quiet environments such as in the laboratory ‒ Pumping speed: 18.1 m³ / h ‒ Ultimate pressure without gas ballast: 7e-3 mbar No venting when stoped due to intgrated check valve ‒ Very low noise level: < 47 dB(A) ‒ Light weight: 23 kg ‒ Integrated Pressure sensor RPT 010 ‒ Interface: RS-485, compatible to Omnicontrol (turbo pump) ‒ Rotation speed variable: 40 - 100% ‒ Active intelligent air-cooling Additional data according brochure ‒ Old Material Number: PD 100 185 -T |  | EL2008 | 5
|  |  | ASCII |  | Status / On-Off / - | EL6022 | 9
VP-2 | dmVP_2 | DM_VP_Pfeifer |  | Vacuum pump, membrane module 2 2000026533 HiScroll Expert Bundle including: HiScroll 18, Omnicontrol 001 with 1 Gauge I/O, exhaust silencer ES 25 L incl. clamps, interface cable and M12 adapter Best for use in quiet environments such as in the laboratory ‒ Pumping speed: 18.1 m³ / h ‒ Ultimate pressure without gas ballast: 7e-3 mbar No venting when stoped due to intgrated check valve ‒ Very low noise level: < 47 dB(A) ‒ Light weight: 23 kg ‒ Integrated Pressure sensor RPT 010 ‒ Interface: RS-485, compatible to Omnicontrol (turbo pump) ‒ Rotation speed variable: 40 - 100% ‒ Active intelligent air-cooling Additional data according brochure ‒ Old Material Number: PD 100 185 -T |  | EL2008 | 5
|  |  | ASCII |  | Status / On-Off / - | EL6022 | 9